        By - ANIL SHARMA
        E.C. - 03048
        Astt. Engg.
        WTP – SP (Ras)
PRESENTATION ON
BOILER WATER CHEMISTRY
&
CHEMICAL CONTROL

---
Objectives of Boiler water treatment
To avoid corrosion & deposition problem.
Generate high purity steam at minimum cost of fuel.
Minimize the blow down to conserve energy.
Avoid premature failure in pre-boiler,boiler & post boiler areas.
Cut maintenance cost.
Prevent down unplanned shut down (break down).
To meet the above objectives we need to control deposits and
corrosion in boiler water system.

---
Common Impurities in boiler water system
Oxygen
Carbon Di – oxide
Calcium & Magnesium Salts
Silica
Iron
Ammonia

---
Water side problems in boiler
Deposition
corrosion
Carry over
Condensate Return line Corrosion
Deposition on turbine blades

---
Deposit Formation
The deposits in boiler are chiefly caused by hardness salts (salts of Ca & Mg )
In boilers,water evaporates continously and concentration of dissolved salts increases progressively. When their conc reach at the saturation point they are thrown out of water in the form of precipitates.If the precipitated matter forms hard coating on the inner walls,it is called scale.
Formation of scales may be due to :
(1).	Deposition of calcium Bicarbonate:
Ca(HCO3)2	CaCO3 + H2O + CO2
This type of Scaling in Low pressure boilers.

---
(2). Deposition of Calcium Sulphate :
Ca + SO4	CaSO4
The solubility of calcium sulphate in water decreases with rise in temperature. Consequently, CaSO4 gets precipitated as hard scale in the boiler.This is the main cause cause of scaling in High pressure boilers.The solubility of CaSO4 is :
3200 ppm at 15 *C
55	ppm at 230*C
27	ppm at	320*C
And completely insoluble in super heated water.
(3). Hydrolysis of magnesium salts:
Mgcl2 + 2H2O	Mg(OH)2	+ 2Hcl

---
(4). Presence of Silica : SiO2 even present insmallquantity, deposits as calcium Silicate & magnesium silicate.
Ca + SiO3	CaSiO3
Mg + SiO3	MgSiO3

---
Disadvantage of Scale Formation :
(1). Wastage of fuel : Scales have low thermal conductivity
so the rate of heat transfer from boiler to inside water is
      greatly decreased.
(2). Over Heating of tubes : Due to scale formation,over heating
       of boiler is to be done in order to maintain a constant steam
       supply. The over heating of the boiler tubes softer & weaker
 and this causesboiler tube failure.

---
CORROSION
Desired protective film in boiler is magnetic iron oxide (Magnetite,
Fe3O4). Boiler steel reacts with water and develops this layer :
Fe + 2H2O	Fe(OH)2 + H2
3Fe(OH)2	Fe3O4 + 2H2O + H2
    (magnetite)
The magnetite is very dark in properly treated system.It will appear
 as a dense black layer on metal surface.Magnetite layer protects
the boiler metal from corrosion.
If oxygen present in water it can convert magnetite to ferric oxide,
which is not protective.
 2Fe3O4 + ½ O2	3Fe2O3
   (Ferric oxide)

---
Caustic Corrosion / Embrittlement
This is a serious form of boiler metal failure, occuring when mild
steel exposed to high alkalinity at high temperature & stress.When
very dilute alkaline boiler water flows into the minute hair cracks &
cervices,water evaporates and NaOH conc build up.
Fe + 2NaOH	Na2FeO2 + H2
  (Sodium Ferroate)
3Na2FeO2 + 4H2O	6NaOH + Fe3O2 + H2
   (magnetite)
6Na2FeO2 + 6H2O + O2	12NaOH + 2Fe2O4
Thus NaOH regenerated & magnetite layer is precipited and metal
Becomes weaker.

---
Condensate System Corrosion
Gases present in boiler feed water will be liberated when the water
is boiled and steam generate.The most corrosive gases in the feed
water are :
 Oxygen
 Carbon Di – oxide
When steam condenses these gases again dissolve and produce
a dilute carbonic acid solution containing oxygen.This solution being
very corrosive will attack steel return pipes and even copper also.
CO2 + H2O	H2CO3
  (carbonic acid)
2H2CO3 + Fe	Fe(HCO3)2 + H2
Fe(HCO3)2	Fe(OH)2 + 2CO2
2Fe(OH)2 + H2O + ½ O2	2Fe(OH)3
2Fe(OH)3	Fe2O3 + H2O
  (ferric oxide)

---
Effects of condensate system corrosion :
If oxygen predominates metal will be pitted
If carbon Di-oxide predominates,metal will be channeled out as grooming.
Prevention :
By maintain condensate pH 8.5 – 9.2
By using Neutralizing Amines to neutralize carbonic acid.
By using filming amines.

---
Carry Over
Carry Over in boiler occur when moisture ( water particles) dissolved solids passes over with steam.
Mechanical Carry Over
        (Priming)
Chemical Carry Over
        (Foaming)
Operating boiler with higher drum level.
Operating below its design.
Sudden load fluctuations.
Improper functioning of steam separator.
High suspended solids.
High TDS in boiler water.
High Alkalinity in boiler water.
Presence of oil/organics
High level of sodium.

---
Effects of Carry Over :
After boiler deposition.
Chocked valves & traps.
Deposition on turbine blades.
If chloride present in steam as a result of carry over, it can
pitting on turbine blades.
Prevention of Carry Over :
The only way to control mechanical carry over (Priming) is to
control boiler operation.
Chemical carry over (Foaming) can be controlled by improving
boiler water quality. However certain anti foams have been
available such as caster oil,Gallic acid,tannin acid,polyamides
and polyalkaline glycol etc.

---
Controlling parameters in steam & water circulating system
The main objectives of boiler water chemical control are :
To maintain blow down in boiler drum.
To minimize corrosion & deposition in steam & water circulating system.
Following parameters should be maintained :
PH
Conductivity / Total dissolve solid
Silica
Oxygen
Hydrazine
Iron & Copper
Hardness &Chlorides

---
Internal Chemical Treatment
The following types of internal chemical treatments are used ,the
selection of which depends upon boiler pressure and ultimate
application of the steam :
Carbonate Treatment
Caustic - Phosphate Treatment
Congruent Phosphate Control Treatment
Polyamine Treatment
All Volatile Treatment
Presently we are using All Volatile Treatment.

---
All Volatile Treatment
This treatment consist three type of chemicals dosings :
(1).Oxygen Scavenger
(2).Neutalizing Amines
(3).Filming Amines
(1).	Oxygen Scavenger
Commonly used oxygen scavengers are :
Sodium sulfite
Hydrazine
DEHA (Diethylhydrdoxlamine)
MEKO (Methylethylketoxime)
Hydroquinone

---
We are using Hydrazine as Oxygen Scavenger :
N2H4 + O2	2H2O + N2
Merits
Volatile oxygen scavenger
Passivated metal surface.
4Fe3O4 + O2	6Fe2O3
6Fe2O3+N2H4	4Fe3O4 + 2H2O + N2
Demerits
80 % conc. Product hazardous & explosive.
Reaction temperature dependent
At high temperature decomposes into Ammonia,which is not good for copper.
toxic & carcinogenic.

---
(2). Neutralizing Amines
The neutralizing Amines work by neutralization of carbonic acid
and increase pH of boiler water system above 8.5
R – NH2 + H2 CO3	R – NH3 + HCO3
There are various types of neutralizing amines,which condense at
various pressure Zones while condensation take place. Commonly
used neutralizing amines are :
Morpholine
Ammonia
Cyclohexamine

---
(3). Filming Amines
Filming amines work by forming a non wettable protective film on
the metal surface Creating a barrier between metal & corrosive
gases. This film provide protection against corrosive gases CO2,
O2 & NH3.
Parameters Range :
Sample PH	Conductivity	Silica
Boiler Feed	8.5 – 9.5	<10	<0.05
CBD	9.1 – 9.6	<100	<2.5
Condensate,	8.5-9.5	<10	<0.02
SHS,DSS
DM tank	8.3 – 9.0	<10	<0.05

---
THANKS