Regn No: ____ _____________

Name: ___________________

(To be written by the candidates)

NATIONAL CERTIFICATION EXAMINATION 2007

FOR

ENERGY MANAGERS & ENERGY AUDITORS

#### PAPER – 3: Energy Efficiency in Electrical Utilities Date: 22.04.2007 Timings: 0930-1230 HRS Duration: 3 HRS Max. Marks: 150

General instructions:

- Please check that this question paper contains 9 printed pages

- Please check that this question paper contains 65 questions

- The question paper is divided into three sections

- All questions in all three sections are compulsory

- All parts of a question should be answered at one place

Section – I:	OBJECTIVE TYPE					         Marks: 50 x 1 = 50

(i)	   Answer all 50 questions

- Each question carries one mark

- Please hatch the appropriate oval in the OMR answer sheet with HB Pencil, as per instructions

|  | What should be the maximum capacitor size to be installed at induction motor terminals for power factor improvement? a) 70% of No load kVAr of the motor b) 80% of No load kVAr of the motor c) 90% of No load kVAr of the motor d)100% of No load kVAr of the motor |
| --- | --- |
|  | The transformer capacity is rated in terms of a) HP b) kVA c) kVAr d) kW |
|  | Which of the following is not likely to create harmonics in an electrical system a) induction motors b) variable frequency drives c) UPS d) soft starters |
|  | For a four pole induction motor operating at 50 Hz, the slip at a shaft speed of 1450 RPM will be a) 0 % b) 3.33 % c) 0.33 % d) none of the above |
|  | A three phase induction motor loaded at less than 50 %,if operated in star mode, will result in a) reduced operating voltage b) electrical downsizing of the motor c) improved efficiency and power factor d) all of the above |
|  | Heat Rate of a thermal power plant is expressed in a) kWh/kCal b) kCal/kWh c) kWh/kJ d) kCal/kVAh |
|  | A 5 kVAr, 415 V rated power factor capacitor was found to be having terminal supply voltage of 430 V. The capacity of the power factor capacitor at the operating supply voltage would be approximately a) 4.65 kVAr b) 5 kVAr c) 5.5 kVAr d) none of the above |
|  | Identify the location of installing capacitor banks, which will result in less reduction in the distribution losses in a factory a) main sub-station bus bars b) distribution panel boards c) motor control centres d) motor terminals |
|  | The nearest kVAr compensation required for changing the power factor of a 1000 kW load from 0.9 lead to unity power factor is a) 900 kVAr b) 485 kVAr c) 1000 kVAr d) none of the above |
|  | Improving power factor at motor terminals in a factory will a) increase active power b) release distribution transformer capacity c) reduce contract demand d) increase motor efficiency |
|  | Use of hard water for inter cooler of a two stage reciprocating air compressor will a) reduce work done for compression b) increase pressure drop in water side c) decrease compressor speed d) reduce air inlet temperature to second stage |
|  | A 500 cfm reciprocating compressor has a loading and unloading period of 5 seconds and 20 seconds respectively during a compressed air leakage test. The air leakage in the compressed air system would be a) 100 cfm b) 125 cfm c) 200 cfm d) none of the above |
|  | A 1000 cfm reciprocating compressor is operating to meet a constant demand of 500 cfm. The least cost energy efficient solution will be a) pulley change b) multi step control c) variable frequency drive d) load and unload |
|  | An air dryer in a compressed air system a) increases dew point of air b) reduces dew point of air c) reduces work of compression d) none of the above |
|  | Which of the following can be used as refrigerant both in vapour compression and vapour absorption system a) R – 11 b) ammonia c) water d) lithium bromide |
|  | The performance of rewinding of an induction motor can be assessed by which of the following factors a) no load current b) stator resistance c) both no load current and stator resistance d) none of the above |
|  | An induction motor rated for 75 kW and 90 % efficiency, operating at full load, will a) deliver 83.3 kW b) draw 75 kW c) deliver 75 kW d) draw 67.5 kW |
|  | With increase in design speed of induction motors the required capacitive kVAr for reactive power compensation for the same capacity range will a) decrease b) increase c) not change d) none of the above |
|  | The flow rate of a reciprocating air compressor can be decreased by a) inlet throttling b) outlet throttling c) decreasing speed d) all of the above |
|  | Which of the following delivers a pulsating output a) reciprocating compressor b) centrifugal compressor c) screw compressor d) roots blower |
|  | Partially closing the outlet damper in a fan system will a) reduce flow b) increase power consumption c) reduce fan static pressure d) all of the above |
|  | Which of the following flow controls in the fan system will change the system resistance curve a) discharge damper b) speed change with variable frequency drive c) speed change with hydraulic coupling d) inlet guide vane |
|  | Parallel operation of two identical fans in a ducted system a) will double the flow b) will double the fan static pressure c) will not double the flow d) will increase flow by more than two times |
|  | Which of the following can also act as a heat pump a) centrifugal pump b) centrifugal compressor c) air conditioner d) none of the above |
|  | A Pitot tube measures------- of the fluid in a ducting system a) velocity b) flow c) the difference between total and static pressures d) static pressure |
|  | A 2 ton air conditioner installed in a room and working continuously for two hours will remove heat of a) 3024 kCals b) 6048 kCals c) 12096 kCals d) 4000 kCals |
|  | Which of the following refrigeration systems uses vacuum for operation - vapour compression system using R-11 - vapour compression system using HFC 134A - vapour absorption system using lithium bromide –water - vapour absorption system using ammonia –water |
|  | The refrigeration load in TR when 100 m3/hr of water is cooled from 12 OC to 7 oC is a) 500 b) 20 c) 165 d) 50,000 |
|  | A fan handling air in a ducted system is an example of a) pure friction head b) pure static head c) combination of static and friction head d) none of the above |
|  | Integrated Part Load Value (IPLV) in a vapour compression refrigeration refers to average of ____with partial loads a) TR/kW b) cooling effect c) kW/TR d) kW |
|  | NPSH available depends on a) pump type b) discharge head c) inlet pipe diameter d) power drawn |
|  | If the wet bulb temperature is 28 oC and cooling water of 28 oC is required, then the most appropriate cooling tower would be a) hyperbolic tower b) cross flow tower c) induced draft counter flow tower with fills d) none of the above |
|  | Higher the COC in a cooling tower, the blow down quantity will a) decrease b) increase c) no change d) it may increase or decrease |
|  | The most appropriate type of fan used for induced draft cooling tower, among the following is a) centrifugal fan with FRP blades b) axial fan with mild steel blades c) centrifugal fan with aluminum blades d) axial fan with aluminium blades |
|  | The blowdown loss in a cooling tower depends on a) TDS in circulating water b) TDS in make up water c) evaporation loss d) all of the above |
|  | In a centrifugal pump the velocity energy is converted to pressure energy by a) impeller b) volute c) discharge duct d) suction duct |
|  | The hydraulic power in a pumping system depends on a) pump efficiency b) motor efficiency c) both motor and pump efficiency d) none of the above |
|  | The friction loss in a pipe carrying a fluid is proportional to the a) fifth power of pipe diameter b) square of the pipe diameter c) fluid velocity d) fluid flow |
|  | The efficiency of a pump does not depend on a) suction head b) discharge head c) motor efficiency d) density of fluid |
|  | When the flow rate increases in a pumping system a) NPSH available increases b) NPSH required increases c) NPSH required decreases d) both NPSH available and NPSH required increases |
|  | When compared to standard motors, energy efficient motors have a) lower slip b) higher shaft speed c) lower starting torque d) all of the above |
|  | Use of soft starters for induction motors results in? a) lower power factor b) lower mechanical stress c) higher maximum demand d) all of the above |
|  | Which of the following is a variable torque load? a) crusher b) centrifugal pump c) machine tool d) vibrating conveyors |
|  | A fluorescent tube light fitted with an electronic choke will a) operate at 25 kHz b) do not need a starter c) increase light output d) all of the above |
|  | A 1100 kVA DG set is delivering 800 kW output. If the flue gas generated is 8 kgs/kWh then the total flue gas flow rate in kg/hr is a) 8800 b) 6400 c) 100 d) 137 |
|  | FRP fans consume less energy than aluminium fans because a) they are lighter b) they deliver less air flow c) they have less system resistance d) they have better efficiencies |
|  | Sodium vapour lamps are not used in indoor applications because they a) have poor colour rendering index b) have poor energy efficiency c) have low lumens output d) occupy a plenty of space |
|  | Which of the following is not a gas discharge lamp a) fluorescent tube lamp b) incandescent lamp c) metal halide lamp d) mercury vapour lamp |
|  | Maximum demand controller installed in a factory will be beneficial only if - the MD charges are for 100 % of the contract demand - maximum demand is more than 5000 kVA - maximum demand is less than 5000 kVA - it is synchronized with the utility meter |
|  | Luminous efficacy of a lamp is given by a) lumens/W b) Lux/W c) W/Lux d) W/lumens |

……. End of Section – I …….

# Section – II: SHORT DESCRIPTIVE QUESTIONS 		     Marks: 10 x 5 = 50

(i)	Answer all Ten questions

(ii)	Each question carries Five marks

S-1	A cast iron foundry has a load of 450 kVA. It has installed two transformers of 500 kVA each. The no load loss and full load copper loss are 710 W and 5300 W respectively. From the energy efficiency point of view the foundry management wants to take a decision on whether to operate a single transformer on full load or two transformers equally sharing the load. What is your recommendation ? Why?

Answer

| 1 x 500 kVA |  |
| --- | --- |
| Transformer loss at 450 kVA | No load loss + [kVA load/Rated kVA]2 x full load loss |
|  | 710 + 4293 |
|  | 5003 W |
| 2 x 500 kVA | 2 x {710 + [225/500]2} x 5300 |
|  | 3567 W |

Two transformers are better because the losses are the least.

S-2	Air at 25,000 m3/hr and at 1.2 kg/m3  density is flowing into an air handling unit of an inspection room. The enthalpy difference between the inlet and outlet air is 10 kJ/kg.    If the motor draw a power of  24 kW at an efficiency of  90%,   find out the kW/TR of the refrigeration system. (1 J = 4.18 Cal.)

Answer

| Refrigeration tonnes | Q x  x (h2-h1) |
| --- | --- |
|  | 25000 x 1.2 x (10 / 4.2) kcal/kg |
|  | 71429kcal/hr |
| TR | 71429/3024 |
|  | 23.6 TR |
| Power input to the compressor | 24 x 0.9= 21.6 kW |
| kW/TR | 21.6/23.6 = 0.915 |

S-3	Air flow measurements using the pitot tube, in the primary air fan of a coal fired boiler gave the following data

Air temperature 				= 33oC

Velocity pressure 				= 43 mmWC

Pitot tube constant, Cp			= 0.9

Air density at 0oC (standard data)		= 1.293 kg /m3

Find out the velocity of air in m/sec

Answer

| Corrected air density | 273 x 1.293 /(273+33) |
| --- | --- |
|  | 1.154 kg/m3 |
| Velocity m/s | Cp x √2 x 9.81 x ∆p x γ / γ |
|  | 0.9 x √2 x 9.81 x 43 x 1.154 / 1.154 |
|  | 24.3 m/s |

S-4	An engineering industry which was operating with a maximum demand of 1200 kVA at 0.9 power factor brought down its demand to 1080 kVA by power factor improvement. Find out the percentage reduction in distribution losses within the plant

Answer

| kW drawn | 1200 kVA x 0.9 |
| --- | --- |
|  | 1080 kW |
| New power factor | 1080/1080 |
|  | =1.0 |
| Distribution loss reduction | 1 – {PF1/PF2}2 x 100 |
|  | 1 - {0.9/1}2 x 100 |
|  | 19 % |

S-5	A system has a static head of 47 meters and friction head of 10 meters. The pump is operating at 1440 RPM. For reducing the flow, the pump speed is reduced to 1100 RPM. What is likely to happen as a result of this ?

Answer

Head developed at 1100 RPM                   -  H2/57 =(1100/1440)2

New head H2                                             -  33.26 m

This head will be insufficient to overcome the static head and hence no flow will occur in the system

S-6	The hot water temperature entering the cooling tower is 39oC. If the wet bulb temperature is  27 oC and the range is twice the approach, find out the cold water temperature and effectiveness of the cooling tower.

Answer

| Range (T1 –T2) = | 2 x Approach (T2 – Twb) |
| --- | --- |
| (39 – T2) | 2 x (T2 – 27) |
| Cold water temperature T2 | 31oC |
| Effectiveness = Range/(Range + approach) | 8/(8+ 4) |
|  | 66.7 % |

S-7	A no load test conducted on a three phase delta connected induction motor gave the  following values:

No load power				= 980 W

Stator resistance per phase at 30oC    = 0.25 Ohms

No load current			= 14.6 A

Calculate the fixed losses for the motor.

Answer

| No load power | 980 W |
| --- | --- |
| Stator resistance at 30oC | 0.25 Ohms |
| No load current | 14.6 A |
| Stator Copper loss at no load | 3 x (14.6/√3)2 x 0.25 Ohms |
|  | = 53.3 W |
| Fixed losses | 980 – 53.3 |
|  | = 926.7 W |

S-8	In a cooling tower, the cooling water circulation rate is 1250 m3/hr.  The operating range is 7oC. If the blowdown rate of the cooling tower is 1 % of the circulation rate, calculate the evaporation loss and COC.

Answer

Evaporation Loss (m3/hr) = 0.00085 x 1.8 x circulation rate (m3/hr) x (T1 –T2)

= 0.00085 x 1.8 x 1250 x 7

= 13.39 m3/hr

Blowdown		     = 12.5 m3/hr

Blowdown = Evaporation loss / (COC – 1)

12.5	=  13.39 / (COC – 1)

COC	= 2.071

S-9	A jockey pump of a fire hydrant system is analysed for efficiency and following data is collected:

Flow - 45 m3/hr , Total head – 100 meters, Power drawn by motor– 23.7 kW, Motor efficiency – 90%

Determine the pump efficiency

Answer

| Hydraulic power | Q (m3/s) x total head (m) x 1000 x 9.81 /1000 |
| --- | --- |
|  | (45/3600) x 100 x 1000 x 9.81/1000 |
| Hydraulic power | 12.26 kW |
| Power input to pump | 23.7 x 0.9 |
|  | 21.33 kW |
| Pump efficiency | 12.26/21.33 |
|  | 57.5 % |

S-10	A 22 kW rated motor driving a lube oil pump is drawing a constant power of 19 kW at 90% efficiency.  If the motor is replaced with an energy efficient motor which operates at 93 % efficiency, find out the annual energy savings at 7000 hours of operation/year.  If the investment is Rs. 30,000/- find out the payback period at Rs.5/kWh energy charges.

Answer

| kW output | 19 x 0.9 |
| --- | --- |
| Energy savings | kW output x [1/New - 1/Old] |
|  | 17.1 [1/0.9 – 1/0.93] x 7000 kWh |
|  | 4290 kWh/year |
|  | 30,000 /(4290 x Rs.5) |
|  | 1.4 years |
|  | 16.8 months |

……. End of Section - II …….

# Section – III: LONG DESCRIPTIVE QUESTIONS		         Marks: 5 x 10 = 50

(i)	Answer all Five questions

(ii)	Each question carries Ten marks

L-1.	List down 10 energy conservation opportunities in a Compressed air system:

- Ensure air intake to compressor is not warm and humid by locating compressors in well-ventilated area or by drawing cold air from outside.  Every 40C rise in air inlet temperature will increase power consumption by 1 percent.

- Clean air-inlet filters regularly. Compressor efficiency will be reduced by 2 percent for every 250 mm WC pressure drop across the filter.

- Keep compressor valves in good condition by removing and inspecting once every six months. Worn-out valves can reduce compressor efficiency by as much as 50 percent.

- Install manometers across the filter and monitor the pressure drop as a guide to replacement of element.

- Minimize low-load compressor operation; if air demand is less than 50 percent of compressor capacity, consider change over to a smaller compressor or reduce compressor speed appropriately (by reducing motor pulley size) in case of belt driven compressors.

- Consider the use of regenerative air dryers, which uses the heat of compressed air to remove moisture.

- Fouled inter-coolers reduce compressor efficiency and cause more water condensation in air receivers and distribution lines resulting in increased corrosion.  Periodic cleaning of inter-coolers must be ensured.

- Compressor free air delivery test (FAD) must be done periodically to check the present operating capacity against its design capacity and corrective steps must be taken if required.

- If more than one compressor is feeding to a common header, compressors must be operated in such a way that only one small compressor should handle the load variations whereas other compressors will operate at full load.

- The possibility of heat recovery from hot compressed air to generate hot air or water for process application must be economically analyzed in case of large compressors.

- Consideration should be given to two-stage or multistage compressor as it consumes less power for the same air output than a single stage compressor.

- If pressure requirements for processes are widely different (e.g. 3 bar to 7 bar), it is advisable to have two separate compressed air systems.

- Reduce compressor delivery pressure, wherever possible, to save energy.

- Provide extra air receivers at points of high cyclic-air demand which permits operation without extra compressor capacity.

- Retrofit with variable speed drives in big compressors, say over 100 kW, to eliminate the `unloaded’ running condition altogether.

- Keep the minimum possible range between load and unload pressure settings.

- Automatic timer controlled drain traps wastes compressed air every time the valve opens. So frequency of drainage should be optimized.

- Check air compressor logs regularly for abnormal readings, especially motor current cooling water flow and temperature, inter-stage and discharge pressures and temperatures and compressor load-cycle.

- Compressed air leakage of 40- 50 percent is not uncommon. Carry out periodic leak tests to estimate the quantity of leakage.

- Install equipment interlocked solenoid cut-off valves in the air system so that air supply to a machine can be switched off when not in use.

- Present energy prices justify liberal designs of pipeline sizes to reduce pressure drops.

- Compressed air piping layout should be made preferably as a ring main to provide desired pressures for all users.

- A smaller dedicated compressor can be installed at load point, located far off from the central compressor house, instead of supplying air through lengthy pipelines.

- All pneumatic equipment should be properly lubricated, which will reduce friction, prevent wear of seals and other rubber parts thus preventing energy wastage due to excessive air consumption or leakage.

- Misuse of compressed air such as for body cleaning, agitation, general floor cleaning, and other similar applications must be discouraged in order to save compressed air and energy.

- Pneumatic equipment should not be operated above the recommended operating pressure as this not only wastes energy bus can also lead to excessive wear of equipment’s components which leads to further energy wastage.

- Pneumatic transport can be replaced by mechanical system as the former consumed about 8 times more energy.  Highest possibility of energy savings is by reducing compressed air use.

- Pneumatic tools such as drill and grinders consume about 20 times more energy than motor driven tools. Hence they have to be used efficiently. Wherever possible, they should be replaced with electrically operated tools.

- Where possible welding is a good practice and should be preferred over threaded connections.

- On account of high pressure drop, ball or plug or gate valves are preferable over globe valves in compressed air lines.

L-2.	A fan is driven by a motor through a belt pulley system. The input power to the fan is 40 kW for a 2500 Nm3/hr fluid flow.   The motor speed is 2990 RPM and its pulley diameter is 200 mm.  The fan pulley diameter is 300 mm. If the flow is to be reduced by 20% by changing the fan pulley size, what should be the diameter of the fan pulley and what will be the power input to the fan ?

Answer

Ratio of fan pulley to motor pulley  	= 300/200 = 1.5

Motor speed                                      	= 2990 RPM

Existing fan speed                            	 = 2990/1.5

= 1993 RPM

Flow delivered at 1993 RPM           	 = 2500 Nm3/hr

Flow at 20 % reduction                    	 = 2500 – 500 = 2000 Nm3/hr

Corresponding fan speed required   	 = (2000/2500) x 1993

= 1594 RPM

New fan pulley size                         	 = (2990/1594) x 200 mm

= 375 mm

Power drawn                                    	= (P1/P2) = (Q1/Q2)3

= (40/P2) = (2500/2000)3

P2                                                                                          = 20.48 kW

L-3.	Draw a sketch of centrifugal pump (head vs flow) characteristic curve incorporating the following. (Draw separate sketches for each of the conditions)

  - System resistance curve (with static and dynamic head) and show the operating point

  - Effect of throttling the pump on head and flow

  - Effect of  pump speed reduction on head and flow

  - Effect of impeller diameter reduction on head and flow

Answer

| System resistance | Effect of throttling |
| --- | --- |
| Pump curve with lower speed | Pump curve with lower impeller diameter |

L-4.	A chemical plant has a contract demand of 2500 kVA with the power supply company. The average maximum demand of the plant is 2100 kVA at a power factor of 0.95. The maximum demand is billed at the rate of Rs.300/kVA. The minimum billable maximum demand is 75 % of the contract demand. An incentive of 0.5 % reduction in energy charges component of electricity bill are provided for every 0.01 increase in power factor over and above 0.95. The average energy charge component of the electricity bill per month for the company is Rs.11 lakhs.

The plant decides to improve the power factor to unity. Determine the power factor capacitor kVAr required, annual reduction in maximum demand charges and energy charge component.  What will be the simple payback period if the cost of power factor capacitors is Rs.800/kVAr.

Answer

| kW drawn | 2100 x 0.95 = 1995 kW |
| --- | --- |
| Kvar required to improve power factor from 0.95 to 1 | kW ( tan 1 – tan 2) |
|  | kW ( tan (cos-1) – tan (cos-2) |
|  | 1995 ( tan (cos-) – tan (cos-) |
|  | 1995 (0.329 - 0) |
|  | 656.36 kVAr |
| Cost of capacitors @Rs.800/kVAr | Rs.5,25,088 |
| Maximum demand at unity power factor | 1995/1 = 1995 kVA |
| 75 % oc contract demand | 1875 kVA |
| Reduction in Demand charges (2100 – 1995) | 105 kVA x Rs.300 |
|  | Rs.31500 x 12 |
|  | Rs.3,78,000 |
| Percentage reduction in energy charge from 0.95 to 1 @ 0.5 % for every 0.01 increase | 2.5 % |
| Monthly energy cost component of the bill | Rs.11,00,000 |
| Reduction in energy cost component | 11,00,000 x (2.5/100) |
|  | Rs.27,500/month |
| Annual reduction | Rs.27,500 x 12 |
|  | Rs.3,30,000 |
| Savings in electricty bill | Rs.7.08,,000 |
| Investment | Rs.5,25,088 |
| Payback period | 5,25,088/7,08,000 |
|  | 0.74 years or 9 months |

L -5   	A cooling tower is operating at a capacity of 31,00,000 kcal/hr and a range of 6oC. The cooling tower pump has a positive suction of 2 m and the discharge pressure shows 3.8 kg/cm2.  The measured motor power is 72 kW and the operating efficiency of the motor is 92%. Find out the efficiency of the pump.

Answer

| Pump flow rate | 31,00,000/6 |
| --- | --- |
|  | 516.6 m3/hr |
| otal head | 38 – 2 = 36 m |
| Hydraulic power | (516.6/3600) x 36 x 9.81 |
|  | 50.6kW |
| Pump input power | 72 x 0.92 |
|  | 66.24 kW |
| Pump efficiency | 50.6/66.24 |
|  | 76 % |

……. End of Section – III ……