Regn No: _________________

Name: ___________________

(To be written by the candidates)

8th NATIONAL CERTIFICATION EXAMINATION

FOR

ENERGY AUDITORS – May, 2009

PAPER – 4: ENERGY PERFORMANCE ASSESSMENT FOR EQUIPMENT AND UTILITY SYSTEMS Date: 24.05.2009 Timings: 1400-1600 HRS Duration: 2 HRS Max. Marks: 100

General instructions:

- Please check that this question paper contains 6 printed pages

- Please check that this question paper contains 16 questions

- The question paper is divided into three sections

- All questions in all three sections are compulsory

- All parts of a question should be answered at one place

# Section - I: 	  SHORT DESCRIPTIVE QUESTIONS		          Marks: 10 x 1 = 10

(i)	Answer all Ten questions

- Each question carries One mark

- Answer should not exceed 50 words

S-1	Between a thermal power plant and a cogeneration plant with a back pressure turbine, which will have a higher heat rate?

###### Ans: A cogeneration plant will have a higher heat rate

S-2	Which loss is considered the most unreliable or complicated to measure in electric motor efficiency testing?

###### Ans. 	The stray load loss, because this loss is only estimated and not measured

S-3 	How is the Overall Heat transfer Coefficient related to surface area?

Ans     Inversely proportional.

S-4	The inclined manometer connected to a pitot tube is sensing which pressure in a gas stream?

Ans:   The difference between total and static pressure (also called velocity pressure)

## S-5	The more fouling fluid should be on which side of a shell & tube heat exchanger and why?

Ans.     Tube side, because it is easier to clean

S-6	For which fuel the sulphur dew point of the flue gases is lower: Furnace oil or Natural gas.

###### Ans : 	Natural gas , because the sulphur content is less

S-7 	What is the range of conversion efficiency of the gasification process using biomass?

###### Ans.	60  - 70 %

S-8 	Calculate the annual power generated from a 100 kW wind turbine generator with a capacity factor of 20% ?

Ans :	100 x .20 x 8760 = 175200 kWhr

S-9 	Define Profitability Index?

Ans.	Profitability Index is defined as the Sum of the discounted net savings to the Capital Cost

S-10 	In a power plant boiler if there is air ingress in the flue duct, which auxiliary system would be most affected?

###### Ans:	Induced Draft Fan

-------- End of Section  - III ---------

# Section - II: 	  Long Questions 					Marks: 2 x 5 = 10

# (i)	Answer all Two questions

# (ii)	Each question carries Five marks

L-1. 	Calculate the blow down rate for a boiler with an evaporation rate of 4 tons/hr, if the maximum permissible TDS in boiler water is 3000 ppm. The   make up water addition rate is 10 % and the feed water TDS is around 250 ppm.

Ans.

Blow down (%) 		= Feed water TDS x % Make upPermissible TDS in Boiler − Feed water TDS

Percentage blow down 	=   250 X 103000 − 250 = 0.91%

If boiler evaporation rate is 4000 kg/hr then required blow down rate is:

=  4000 x 0.91/ 100

= 36.4 kg/hr

OR

Blow down (%) 		=Feed water TDS x % Makeup/ Permissible TDS in Boiler

Percentage blow down 	=  250 x 10/ 3000	= 0.83%

If boiler evaporation rate is 4000 kg/hr then required blow down rate is:

=  4000 x .83/100 	= 33.2 kg/hr

L-2 	The suction head of a pump is 5 m below the pump centre line.  The discharge pressure is 3 kg/cm2.  The flow rate of water is 100 m3 /hr.  Find out the pump efficiency if the actual power input at the shaft is 15 kW.

Ans: 	Discharge Head	         =	3 kg/cm2

= 30 metre head.

Suction Head		        =	- 5 metre.

Total Head 		        =	30 – (-5) = 35 metre

Hydraulic Power	        =	(100/3600) x 1000 x 9.81 x 35/1000

= 9.53 kW

Pump Efficiency	        =	100 x 9.53 / 15 = 63.5 %

-------- End of Section  - II ---------

# Section - III: 	   Numerical Questions 				Marks: 4 x 20 = 80

- Answer all Four questions

- Each question carries Twenty marks

N-1  	A fertilizer plant consuming 100TPH of saturated steam at 45 kg/sq.cm pressure has been using Indian coal as fuel to the boiler and is now switching over to imported coal.

Typical ultimate analysis of the two types of coals:

------------------------------------------------------------------------------------------------

Parameters                    Indian coal                        Imported coal

%                                         %

-------------------------------------------------------------------------------------------------

Carbon                          	41.11                                	58.96

Hydrogen                       	2.76 	                                	4.16

Nitrogen                          	1.22                                    	1.02

Oxygen                        	9.89                                    	11.88

Sulphur		0.41		0.56

Moisture                    		5.98                                    	9.43

Ash                             	38.63                                  	13.99

---------------------------------------------------------------------------------------------------

GCV (kCal/kg)            	4,000                         	5,900

Determine:

(i)	Coal requirement in each case

(ii)	Calculate % dry flue gas losses in both cases

Assume: in both cases

Flue gas temperature 	= 200oC

Ambient temperature 	= 30oC

Enthalpy of steam		= 668 kCal/kg

Feed water temperature 	= 80oC

Specific heat of flue gases 	= 0.23

Boiler efficiency with Indian coal 			 = 70%

Boiler efficiency with Imported coal 		 = 75%

Oxygen content in flue gases with Indian coal 	 = 10%

Oxygen content in flue gases with Imported coal = 4%

### Answer

Coal requirement

| #### Q = | Steam (q) x (hg – hf) |
| --- | --- |
|  | Efficiency x GCV |

Indian coal

| Q= Imported coal #### Q =; 100,000 x (668 – 80). 0.75 x 5900. 13.28 T/hr | 100,000 x (668 – 80) |
| --- | --- |
|  | 0.70 x 4000 |

21.0 T/hr

##### Find theoretical air requirement

= [(11.6 x C) +  {34.8 x(H2 - O2/8)} + (4.35 x S)]     kg / kg of coal

100

For Indian coal

= [(11.6 x 41.11) +  {34.8 x(2.76 – 9.89/8)} + (4.35 x 0.41)]     = 5.3  kg / kg of coal

100

For Imported Coal

= [(11.6 x 58.96) +  {34.8 x(4.16 – 11.88/8)} + (4.35 x .56)]     = 7.79 kg / kg of coal

100

Excess air percentage in Indian coal   = 10 x 100/ 21 - 10  = 90.9%

Excess air percentage in Imported coal = 4 x 100/ 21 – 4    = 23.5%

Actual mass of air (AAS)

Kg/ kg of coal   		= 5.3 x 1.9 = 10.07 kg (Indian coal)

= 7.79 x 1.235= 9.62 kg (Imported coal)

Heat loss in dry flue gas	= M x CP (Tf – Ta) x 100

GCV

-	Indian coal	= (10.07+1) x 0.23 x (200 – 30) x 100

4000

= 10.8%

-	Imported coal 	= (9.62+1) x 0.23 x (200 – 30) x 100

5900

= 7.04%

Alternatively:

Indian Coal : Mass of dry flue gas = Mass of (CO2 + SO2 + N2 + O2) in flue gas

+ N2 in air we supply

= 0.4111x44  + 0.0041x64 + 0.0122 + 10.07x77 + {(10.07-5.3)x23/100}

12		32			100

= 10.38 kg/kg of fuel.

Imported Coal:

= 0.5896x44  + 0.0056x64 + 0.0102 + 9.62x77 + {(9.62- 7.79)x23/100}

12		32			100

= 10.01 kg/kg of fuel.

Heat loss dry flue gas:

Indian Coal: = 10.38 x 0.23 x (200 – 30) x 100  = 10.1%

4000

Imported Coal: = 10.01 x 0.23 x (200 – 30) x 100 = 6.63%

5900

N-2	The cost and estimated savings data for an energy saving retrofit project is given in table below.

| Retrofit cost | Energy & demand savings | Maintenance cost savings |
| --- | --- | --- |
| Rs. 1,20,000 | 6000 kWh/year & Rs.3800/year as demand charges | Annual maintenance cost savings will be Rs. 2000/-. |

- The key data is given below:

- Energy savings are based on Rs 3.00/kWh

- No changes in energy rates for 10 years

- The project has a 10 year life period

Calculate NPV for the upgrade option against 12% discount rate.

| Ans | ###### Cost of Energy & demand savings per year = 6000 x 3 + 3800 = Rs 21,800 The cash flow detail for ten year duration is given below: Year; Retrofit cost; Cost of Energy & demand savings; Maintenance cost savings; Cash flow; Discount Factor for 12%; Present Value. 0; 120000; 0; 0; -120000; 1.000; -120000. 1; 0; 21800; +2000; 23800; 0.893; 21253.4. 2; 0; 21800; +2000; 23800; 0.797; 18968.6. 3; 0; 21800; +2000; 23800; 0.712; 16945.6. 4; 0; 21800; +2000; 23800; 0.636; 15136.8. 5; 0; 21800; +2000; 23800; 0.567; 13494.6. 6; 0; 21800; +2000; 23800; 0.507; 12066.6. 7; 0; 21800; +2000; 23800; 0.452; 10757.6. 8; 0; 21800; +2000; 23800; 0.404; 9615.2. 9; 0; 21800; +2000; 23800; 0.361; 8591.8. 10; 0; 21800; +2000; 23800; 0.322; 7663.6. Total; 20,000; 1,38,000; 14,493.8. The NPV for the upgrade option against 12% interest rate = Rs 14,494/- |
| --- | --- |

N-3	A pharma unit had installed a centralized refrigeration system of 120 TR Capacity several years ago. The refrigeration system operators 24 hours a day, 300 days per annum and the average electricity cost is Rs. 4.5/ kWh. The following are the key operational parameters.

- Compressor operating current and power factor	:	153 amps. 0.9 pf

- Condenser pump operating current and power factor:	43 amps, 0.88 pf

- Chiller pump operating current and power factor	:	25 amps, 0.9 pf

- CT fan operating current and power factor		:	20 amps. 0.65 pf

- ΔT across the chiller (evaporator)			:	3.5OC

- Chilled water flow					:	23 Lit  / Sec

- Total head developed by chiller pump		: 	35 mtrs.

- Condenser water flow					:	41 Lit / Sec

- Total head developed by condenser pump		:	30 mtrs.

PS: all the motors operate at 415 Volts:

Calculate:

- The power consumed by the compressor, condenser pump, chiller pump and CT fan.

- TR developed by the system

- Specific power consumption i.e. overall kW/TR and COP and Energy Efficiency ratio (EER)

- Combined efficiency (motor and pump) of condenser and chiller pumps

The unit proposes to replace the existing condenser and chilled water pumps with efficient pumps having a combined efficiency of 65%. Also the unit goes in for condenser cleaning by which the power consumption of compressor has reduced by 10%.

Calculate:

- The envisaged power consumption of the compressor, condenser and chiller pump

- Hourly energy savings (compressor, condenser and chilled water pump)

- Annual energy and equivalent monetary savings (compressor, condenser and chilled water pump)

- Specific power consumption i.e. overall kW/ TR and COP and Energy Efficiency ratio (EER)

Answer

Present Condition:

Compressor Power		:	99 kW

Condenser Pump Power		:	27.2 kW

Chiller Pump Power		:	16.2 kW

CT Fan		:	9.4 kW

Total Power		:	151.8 kW

TR Devp		:	(23 * 3600 * 3.5 / 3024) = 95.83

Sp. Power		:	1.58 kW/ TR

Compressor kW/TR		:	99/95.83 = 1.03 kW/TR

COP		:	3.516 / 1.03	= 3.41

EER		:	12 / 1.03	= 11.65

Condenser pump efficiency		:	44.4%

Chiller pump efficiency		:	48.8%

Proposed condition:

Compressor Power	:	89 kW

Condenser Pump Power	:	18.6 KW

Chiller Pump Power	:	12.2 kW

CT Fan	:	9.4 kW

Total Power	:	129.2 kW

TR Devp	:	95.83 TR i.e. (23 LPS * 3600 Sec * 3.5 / 3024)

Sp. Power	:	1.35 kW/ TR

Compressor kW/TR	:	89/95.83 = 0.93 kW/TR

COP	:	3.516 / 0.93 	=  3.78

EER	:	12 / 0.93	= 12.90

|  | Compressor | Condenser Pump | Chiller Pump |
| --- | --- | --- | --- |
| Hourly energy savings – kWh | (99-89) = 10 | (27.2-18.6) = 8.6 | (16.2–12.2) = 4.0 |
| Annual energy savings – kWh (7200 hrs) | 72000 | 61920 | 28800 |
| Annual monetary savings (Rs) @ Rs. 4.5/ kWh | 324000 | 278640 | 129600 |

N-4	Government of India has undertaken various schemes to promote energy efficiency in the country. In the last one year implementation of these schemes have resulted in savings as given below:

| S. No. | Name of the scheme | Energy Source | Units | Quantity Saved |
| --- | --- | --- | --- | --- |
| 1 | Energy Efficiency in Buildings | Electricity from grid | Million kWh | 62 |
| 2 | Energy Efficiency in Industries | Electricity from Grid | Million kWh | 1216 |
|  |  | Electricity from Captive Diesel Generation | Million kWh | 1000 |
|  |  | Fuel Oil | Lakh kilo liter | 1.85 |
|  |  | Coal | Lakh tons | 3.5 |
|  |  | Natural Gas | Lakh Sm3 | 15728 |
| 3 | Domestic Appliance Labelling Scheme | Electricity from grid | Million kWh | 1374 |
| 4 | Various other schemes as reported by different States exclusive of GOI schemes | Electricity from grid | Million kWh | 635 |
|  |  | Thermal Energy Saved | MTOE | 80702 |

Given that:

1 kWhr 				= 860 kCal

GCV of Coal 				= 4000 kCal/ kg

GCV of Natural Gas 			= 8500 k Cal/Sm3

Assuming GCV of fuel Oil & Diesel 	= 10000 kCal/kg

Specific gravity of fuel Oil 		= 0.94, & for diesel 0.85

Assume average Transmission and Distribution Losses in India = 20%

Average Plant Load Factor 		= 70%

Specific diesel consumption 		= 3.5 kWh/ltr

Calculate : i) Total Energy Saved in MTOE (metric ton oil equivalent)

ii) Total Generation Capacity Avoided (in MW) in the country because of energy savings due to grid connected power.

Ans:  Total Electricity Saved from grid = 62 + 1216 + 1374 + 635    = 3287 million kWh

MTOE  due to electrical savings = ( 3287 x 10 6 x 860 ) / 10 7

= 282682 MTOE

MTOE  due to coal savings= ( 3.5 x 10 5 x 1000 x 4000 ) / 10 7

= 140000 MTOE

MTOE  due to natural gas savings= ( 15728 x 10 5 x 8500 ) / 10 7

= 1336880 MTOE

MTOE  due to Fuel oil savings = ( 1.85 x 105 x 0.94  x 1000 x 10000 ) / 10 7

= 173900 MTOE

MTOE due to captive diesel generation = 1000 x 106 x 0.85 x 10000 / 3.5 x  107

= 242857 MTOE

Total MTOE = 282682 + 140000 + 1336880 + 173900 + 80702 + 242857 = 2257021 MTOE

ii) Grid Electricity Saved = (62 +1216 + 1374 + 635 ) million k Wh =

= 3287 x 10 6  kWh

Therefore Avoided Capacity =   3287 x  10 6    / ( 0.70  x .80 x 365 x 24 x 1000  )

= 670 MW

-------- End of Section  - III ---------